## Slide 1: SIMATIC S7-1200 Basic Controller in the TIA Portal
Technical slides
Unrestricted © Siemens AG 2017
Notes: S7-1200 and TIA Portal Software
The S7-1200 is the successor to the S7-200 and has been developed for the global market.
The SIMATIC S7-200 products have been discontinued since 1/10/2013. They will still be available as new parts for one further year until 1/10/2014. They can then be ordered as spare parts for a further 9 years. Products from the SIMATIC S7-1200 range should be used with the STEP 7 Basic configuration software for new applications.
The TIA Portal is used with STEP 7 Basic for programming the S7-1200 (ordered separately from the hardware). - This includes program editors for the COP (Contact Plan), FUP (Functional Plan) and SCL (Structured Control Language).
- AWL programming (for the instruction list) is not supported.
- It includes WinCC Basic for configuring the HMI Basic Panels. - No separate USB license stick is required. The software is automatically activated during installation.
Windows Explorer and data compression can be used to copy the project directory structure in order to move project files between PCs.
Approvals for the S7-1200
The S7-1200 hardware has received the approvals required for the US and European markets.
The S7-1200 has cFMus approval for explosive areas:
The Factory Mutual Research FM: Approval Standard Class Number 3600 and 3611 Approved for use in: - Class I, Division 2, Gas Group A, B, C, D, Temperature Class T3C, Ta = 60°C - Class I, Zone 2, IIC, Temperature Class T3 , Ta = 60°C
The S7-1200 hardware has the cULus and CE approvals.

## Slide 2: SIMATIC Controller S7-1200
Efficient engineering
+
Security Integrated.
+
Diagnostics
+
Technology Integrated
+
Innovative design and easy
to use
+
Safety Integrated
+
High performance
+

## Slide 3: SIMATIC S7-1200 configured in the TIA Portal Fits perfectly
Modular space-saving controller for automation systems requiring simple or extended functionality in the area of logic, HMI and networking.
  Perfect for stand-alone and interconnected machines and cost-effective automation solutions
  Simple integration into interconnected systems and into systems that require one or more HMI devices
  Extended functionality for small motion control systems and small process applications
Controller, HMI and networking: everything developed in one software architecture

## Slide 4: SIMATIC S7-1200 configured in the TIA Portal Modular and powerful.
  Uniform software for hardware, HMI and network configuration – through a uniform user concept, common data storage and centralized services
  Code modularity – allows existing automation parts such as an SCL program to be reused in another product series.
  Common project concept – Automatic detection between multiple controllers with multiple HMI devices without having to maintain separate user programs for every device. One user program is possible for the entire system.
Shorter engineering and service periods through an efficient uniform programming environment.
Notes: Three Areas of Innovation
System Architecture
The system architecture is designed from the Inside Out not the Outside In. The combined design of the controller hardware, the HMI hardware and all firmware share a common set of intelligence with the Engineering Software, eliminating traditional barriers of interoperability between common automation devices (Controllers, HMI, Networks). This unified system architecture was traditionally only available in larger, specialized or PC-Based control platforms NOT in the smaller PLC classes.
This Integrated Automation design provides: **Pointing to the hardware images across the top**
Auto-detection between multiple controllers with multiple HMIs without the need to maintain separate user programs for each. There can be one user program for the system, or libraries you assemble for a modular system.
No need to use separate standalone utilities (and maintain separate configurations) for PID Loop Tuning, Motion Control using PLC Open instructions. Everything is built into the engineering software and included with the user program.
**Pointing to the software screen images to the left**
Step7 Basic represents one engineering software for Logic, HMI and Networking with a Common Editor. All navigation, icons, and menus are consistent throughout its Views. Easy to learn and maintain. No other Micro or Nano PLC competitor can provide this.
**Pointing to the PG Engineering Station middle-bottom**
Step7 Basic provides Instant-On Connections over Ethernet to all supported devices on the network. It is graphical and requires no configuration or multiple instances to connect to everything.
All user program documentation for the controller logic is stored in the CPU (symbols, network comments, descriptions, etc.) Offline program not required to see documentation, much easier and quicker maintenance
The result is a Common “Core Intelligence” for integrated automation in the Compact Controller class. Unique for the Micro or Nano PLC category

## Slide 5: SIMATIC S7-1200 compact controllers Modular and powerful.
  Integrated PROFINET/Ethernet Port – No additional proprietary programming cable and no Ethernet extension module required  reducing space requirements and costs.
  Scalable extension concept using modular boards – Signal boards for additional I/O ports, with no extra space required for the CPU. If you just need one RTD input: no problem!
  Integrated digital I/O, analog I/O and Motion Control I/O – makes additional hardware superfluous; thereby reducing space requirements and costs.
Integrated PROFINET, modular boards and integrated I/O mix reduce costs.
Notes: 2. Hardware Innovation
More built-in hardware functionality within the CPU than any other Siemens Micro PLC. Integrated Ethernet, Analog I/O, Motion Control I/O, & SD Memory interface.
– eliminating the need for additional hardware; reducing space and cost
**Pointing to CPU and Graphics along the bottom**
Significantly reduced width compared to other MicroPLCs, including the S7-200. (e.g. increasing an enclosure width by only 6-inches can sometimes double its price)
Inputs on the top and Outputs on the bottom is an efficient design with smaller gage input wiring having longer runs to the top and shorter heavier gage loads on the bottom. More practical panel layout and lower wiring cost.
Full size 14AWG terminal blocks; many other MicroPLCs have barrier strip terminals and/or smaller block terminals, more difficult to wire
Durable industrial plastic with a nylon composite mix, not brittle ABS plastic that can break/crack easily like other Micro PLCs (AutomationDirect)
2AI channels are separate I/O points, not simply 2 configurable discrete points (loose no discrete points when using built-in 2AI channels)
Removable terminal blocks on both CPU and Signal Modules
Industrial grade metal RJ45 Ethernet port
Standard SD memory interface not a proprietary hardware design. Can insert SD memory into PG/PC and copy program without using an S7-1200 CPU
Unique front panel signal board interface for 2-DI/2-DO signal board or 1-AO. Add I/O without increasing panel space.
**Pointing to the Fully Assembled System**
The hardware design combines the best of a classic Brick MicroPLC design with top/bottom terminals for easy wiring along with modular expansion of the I/O to the right and Communication/Specialty Modules to the left. This provides an efficient panel layout with higher-current/inductive I/O loads on the right away from the communication signals on the left. Reduces the possibility of noise problems.
Resulting in compatible interfaces for easy integration, startup and reduced cost

## Slide 6: Design and handling S7-1200 CPU
PROFINET interface (1 or 2 ports)
S7-1200: Modular. Powerful
Digital outputs (DC or relay)
Removable connectors
Integrated HSCs & PTOs/PWMs
Optional memory extension
Analog inputs
Modular board concept
Digital inputs

## Slide 7: Design and handling S7-1200 CPU - setup
Power supply
Slot for a memory card below the upper cover flap
Plug-in terminal block for user wiring (behind the cover flaps)
Status LEDs for the integrated I/O
PROFINET connection (on the bottom of the CPU)

## Slide 8: Design and handling Set-up and extension options - maximum
S7-1200: variable extension and set-up options for differing requirements
CPU 1214C / 1215C / 1217C
CM/CP
CPU
CPU 1212C
SM
CPU 1211C
1 Board
Notes: S7-1200 | CPU Digital I/O | CPU Analog I/O | CPU Power supply and I/O type
CPU 1211C | 6 IN - 4 OUT | 2 IN | Available in three designs for CPU power supply / input / output type DC / DC / DC AC / DC / relay DC / DC / relay
CPU 1212C | 8 IN – 6 OUT | 2 IN | 
CPU 1214C | 14 IN -10 OUT | 2 IN | 
CPU 1215C | 14 IN -10 OUT | 2 IN - 2 OUT | 
CPU 1217C | 10 IN sink/source 4 IN 1.5V differential 6 OUT MOSFET Sourcing 4 OUT 1.5V differential | 2 IN - 2 OUT | Only available as DC / DC / DC
S7-1200 communication options
Integrated PROFINET network connection
CB 1241 RS485
CM 1241 RS232
CM 1241 RS485
CM 1241 RS422/485
CP 1242-7 GPRS
CM 1242-5 PROFIBUS slave
CM 1243-5 PROFIBUS master
CM 1243-1 DNP3 Ethernet WAN
CM 1243-1 IEC Ethernet WAN
CP 1243-1 Ethernet WAN (Firewall and VPN)
CM 1243-2 AS-I Master
RF120C RFID
TS Adapter and modular TS Adapter for SIMATIC Teleservice

## Slide 9: Design and handling Extension module assembly
Expansion
Remove backplane bus cover
Insert SM into standard mounting rails
Guide the SM to the adjacent module
Lock the standard rail mounting clamp
Guide the bracket for the bus connector contact to the left towards the adjacent module
Loosen the bus connector contact by pushing the bolt to the right
Move SM right onto standard mounting rail
Unlock standard mounting rail clamp
SM out of standard mounting rail
Installation

## Slide 10: Design and handling CPU – 17 Versions incl. failsafe
S7-1200: variable extension and set-up options for differing requirements
CPU 1217C DC/DC/DC
CPU 1211C
…DC/DC/DC
…DC/DC/RLY
…AC/DC/RLY
CPU 1212C
…DC/DC/DC
…DC/DC/RLY
…AC/DC/RLY
CPU 1214C
…DC/DC/DC
…DC/DC/RLY
…AC/DC/RLY
CPU 1215C
…DC/DC/DC
…DC/DC/RLY
…AC/DC/RLY

## Slide 11: Design and handling CPU dimensions
CPU 1217C DC/DC/DC
CPU 1211C
CPU 1212C
CPU 1214C
CPU 1215C
S7-1200: variable extension and set-up options for differing requirements
90
100
75
90
100
75
110
100
75
130
100
75
150
100
75

## Slide 12: Design and handling Optional CPU functional enhancements using boards
Board type | Characteristics
SB 1221 | 4 DI, DC 5V, HSC with up to 200 kHz available for use
 | 4 DI, DC 24V, HSC with up to 200 kHz available for use
SB 1222 | 4 DQ DC 5V, 0.1 A, PWM with up to 200 kHz, PTO with up to 100 kHz available for use
 | 4 DQ DC 24V, 0.1 A, PWM with up to 200 kHz, PTO with up to 100 kHz available for use
SB 1223 | 2 DI, DC 5V, 2 DQ DC 5V, 0.1 A, HSC with up to 200 kHz, PWM with up to 200 kHz, PTO with up to 100 kHz available for use
 | 2 DI, DC 24V, 2 DQ DC 24V, 0.1 A, HSC with up to 200 kHz, PWM with up to 200 kHz, PTO with up to 100 kHz available for use
 | 2 DI, DC 24V, 2 DQ DC 24V, 0.1 A
SB 1231 AI | 1 AI, ±10VDC (12 bit) or 0…20 mA
SB 1231 RTD | 1 AI RTD, PT 100 and PT1000
SB 1231 TC | 1 AI thermal elements type J or K
SB 1232 AQ | 1 AO, ±10VDC (12 bit) or 0…20 mA (11 bit)
CB 1241 | RS485 communication board
BB 1297 | Battery board for real-time clock long-term buffering (without CR1025 battery)

## Slide 13: Design and handling Digital signal modules and signal boards
SM 1221 digital input |  | SM 1223 digital input/output |  | SM 1222 digital output | 
45 mm | 8 DI, 24V DC 16 DI, 24V DC SINK/SOURCE | 45 mm | DI 8x 24 VDC, DQ8 x RLY DI 8/DQ 8 24 VDC | 45 mm | DQ 8x RLY DQ 8x 24 VDC DQ 16x RLY
 |  | 70 mm | DI 16x 24 VDC, DQ 16x RLY DI 16/DQ 16 24 VDC DI 8 x120/230 V AC / DQ 8 x relays | 70 mm | DQ 8x RLY (changeover contact) DO 16x 24 VDC
SB 1221 digital input |  | SB 1223 digital input/output |  | SB 1222 digital output | 
 | 4DI, 5VDC 200kHz 4DI, 24VDC 200kHz Reading M |  | 2DI/2DQ 24VDC 2DI/2DQ, 5VDC 200kHz 2DI/2DQ, 24VDC 200kHz |  | 4DQ, 5VDC 200kHz 4DQ, 24VDC 200kHz

## Slide 14: Design and handling Analog signal modules and signal boards
SM 1231 analog input |  | SM 1234 analog input/output |  | SM 1232 analog output | 
45 mm | 4 AI 13 bit, ±10V, ±5V, ±2.5V, or 0-20/4-20 mA 8 AI 13 bit, ±10V, ±5V, ±2.5V, or 0-20/4-20 mA 4 AI 16 bit, ±10V, ±5V, ±2.5V, or 0-20/4-20 mA 4 AI 16 bit TC 8 AI 16 bit TC 4 AI 16 bit RTD 8 AI 16 bit RTD | 45 mm | 4 AI 13 bit, ±10V ±5V or ±2.5V or 4-20 mA / 2 AQ 14 Bit, ±10V or 4-20 mA | 45 mm | 2 AQ, ±10V, 14 bit or 0 – 20 or 4 - 20 mA, 13 bit 4 AQ, ±10V, 14 bit or 0 – 20 or 4 - 20 mA, 13 bit
SB 1231 analog input |  |  |  | SB 1232 analog output | 
 | 1 AI, 12 bit ±10VDC or 0-20 mA 1 AI, 16 bit RTD (Pt) 1 AI, 16 bit TC (type: J,K; ± 80 mV) |  |  |  | 1 AQ, ±10V (12 bit) or 0 - 20 mA (11 bit)

## Slide 15: Design und Handling Features SM 1238 ENERGY METER 480VAC
SM1238
Energy Meter 480VAC
Article Nr.: 6ES7238-5XA32-0XB0
Power supply
Inputs for voltage measurement
L1 – L3 directly connected to the inputs without voltage transformer: 110V – 480V PH – PH
Inputs for current measurement
L1 – L3 connected indirect with current transformer; 1 or 5A
Voltage transformers are supported if necessary
Set transformer ratio for voltage > 480 V
N
L1
45 mm width
Diag- LED
Support of TN and TT networks
backup of measured data: NV memory
HSP f. TIAP V13 SP1, ≥ CPU V4.1
Max. 8 SM 1238 at one CPU
L1 and N directly connected to voltage input for power supply
No supply with 24V of the CPU

## Slide 16: Design und Handling SM 1238 ENERGY METER 480VAC Properties
Measurement of electrical variables from single-, two- and three-phase supply networks
Max. nominal voltage between 2 outer con-ductors 480 VAC (max. phase voltage 277 VAC)
Recording of:
    Voltages
    Currents
    Phase angles
    Power
    Energy / electrical work
    Frequencies
    Minimum and maximum values
    Power factors
    Operating hours
    Energy counter
The module supports the following functions:
Firmware update
I&M identification data
Reconfiguration in RUN
Diagnostics interrupts
Measuring access method (Module variants)
Read acyclically via data record
read cyclically for 19 defined data sets
EE@IndustryE0, E1, E2 and E3

## Slide 17: Design and handling SIMATIC S7-1200 with FW4.2
Connection resources
Integrated Analog I/O
High-Speed Counter
Integrated Digital I/O
PROFINET Ports
Bit performance
Work memory / int. load memory
CPU type
1212FC
85 ns
100kB 2 MB
8/6
6
2/-
38
1214C
85 ns
100kB 4 MB
14/10
6
2/-
38
1211C
50 kB 1 MB
6/4
6
85 ns
2/-
38
1215FC
85 ns
150 kB 4 MB
14/10
6
2/2
38
1217C
85 ns
150 kB 4 MB
14/10
6
2/2
38
1215C
85 ns
125 kB 4 MB
14/10
6
2/2
38
1214FC
85 ns
125kB 4 MB
14/10
6
2/-
38
1212C
85 ns
75kB 2 MB
8/6
6
2/-
38
SIMATIC S7-1200 CPU

## Slide 18: Design and handling S7-1200 CPU features (1/4)
1) See Technical Specifications for the number of inputs or outputs allowed on simultaneously. Some models are de-rated for 60°C horizontal mounting and 50°C vertical mounting
 | CPU 1211C | CPU 1212C | CPU 1214C | CPU 1215C | CPU 1217C
CPU type | DC/DC/DC, AC/DC/RLY, DC/DC/RLY |  |  |  | DC/DC/DC
Work memory, integrated | 50 KB | 75 KB | 100 KB | 125 KB | 150 KB
Load memory, integrated | 1 MB |  | 4 MB |  | 
Retentive memory, integr. | 10 KB |  |  |  | 
Marker(M) | 4 KB |  | 8 KB |  | 
Integrated Digital I/O 1) | 6 inputs / 4 outputs | 8 inputs / 6 outputs | 14 inputs / 10 outputs |  | 
RS485 Differential I/O |  |  |  |  | 4 / 4 (1 MHz)
Integrated Analog I/O | 2 inputs |  |  | 2 inputs / 2 outputs | 
Process image size | 1024 bytes for inputs / 1024 bytes for outputs |  |  |  | 
Board (SB/CB) Expansion | 1 max. |  |  |  | 
Extension: Signal Module | none | 2 max. | 8 max. |  | 
Max. Local I/O – Digital | 14 | 82 | 284 | 284 | 
Max. Local I/O – Analog | 3 | 19 | 67 | 69 | 

## Slide 19: Design and handling S7-1200 CPU features (2/4)
1) lower frequency with HSC configuration in 2-phase operation (A/B counter operation)
2) CPU versions with relay outputs require a digital signal board (SB) with use of pulse outputs
 |  | CPU 1211C | CPU 1212C | CPU 1214C | CPU 1215C | CPU 1217C
High-speed counters | Total | Max. 6, configured for the use of integrated or SB inputs |  |  |  | 
 | 1 MHz | none |  |  |  | 4
 | 100 / 80 kHz 1) | 6 |  |  |  | 
 | 30 / 20 kHz 1) | - | 1 | 3 |  | 
 | 200 kHz | with SB 1221 DI 4x 24 VDC 200 kHz or SB 1221 DI 4x 5 VDC 200 kHz |  |  |  | 
Pulse outputs 2) | Total | Max. 4, configured for the use of integrated or SB outputs |  |  |  | 
 | 1 MHz | none |  |  |  | 4
 | 100 kHz | 4 |  |  |  | 
 | 20 kHz |  |  |  |  | 
Pulse Catch Inputs |  | 6 | 8 | 14 |  | 

## Slide 20: Design and handling S7-1200 CPU features (3/4)
 | CPU 1211C | CPU 1212C | CPU 1214C | CPU 1215C | CPU 1217C
Execution time Binary instruction | 0.08 μs/operation |  |  |  | 
Execution time Word instruction | 1.7 μs/operation |  |  |  | 
Execution time Real number instruction | 2.3 μs/operation |  |  |  | 
PROFINET Ports | 1 |  |  | 2 | 
Type | RJ45 |  |  |  | 
Data rate | 10/100 MBaud |  |  |  | 
Additional communication modules | 3 max |  |  |  | 
Ambient conditions - Operation | -20°C to 60 °C horizontal assembly / -20°C to 50°C vertical assembly (observe derating conditions for individual modules) |  |  |  | 
Real-time clock buffering | 20 days, typ./min. 12 days at 40°C (maintenance-free high-performance capacitor) |  |  |  | 
Dimensions W x H x D (mm) | 90 x 100 x 75 |  | 110 x 100 x 75 | 130 x 100 x 75 | 150 x 100 x 75

## Slide 21: Design and handling S7-1200 CPU features (4/4) Integrated I/O and SB I/O options
 |  | 1211C | 1212C | 1214C | 1215C | 1217C
DI digital input | CPU | 6 | 8 | 14 |  | 
 | SB | ≤ 4 (optional) |  |  |  | 
including HSC high-speed counters | CPU or SB inputs | 6 |  |  |  | 
DQ digital output | CPU | 4 | 6 | 10 |  | 
 | SB | ≤ 4 (optional) |  |  |  | 
AI Analog input | CPU | 2 |  |  |  | 
 | SB | 1 (optional) |  |  |  | 
AQ analog output | CPU | - |  |  | 2 | 
 | SB | 1 (optional) |  |  |  | 
Technological outputs |  |  |  |  |  | 
PWM / PTO pulse output | CPU or SB outputs | 4 |  |  |  | 
 | Position-controlled axes (PROFIdrive, analog) | 8 |  |  |  | 
Notes: S7-1200 I/O options |  | 
Digital and analog signal modules | SM 1221 digital IN | DI 8 x 24 VDC
 |  | DI 16 x 24 VDC
 | SM 1222 digital OUT | DQ 8 x relays
 |  | DQ 8 x O/C relays
 |  | DQ 8 x 24 VDC
 |  | DQ 16 x relays
 |  | DQ 16 x 24 VDC
 | SM 1223 digital IN/OUT | DI 8 x 24 VDC / DQ 8 x relays
 |  | DI 16 x 24 VDC / DQ 16 x relays
 |  | DI 8 x 24 VDC / DQ 8 x 24 VDC
 |  | DI 16 x 24 VDC / DQ 16 x 24 VDC
 |  | DI 8 x 120/230 VAC / DQ 8 x relays
 | SM 1231 analog IN | AI 4 x 13 bit, AI 8 x 13, AI 4 x 16
 | SM 1232 analog OUT | AQ 2 x 14 bit, AQ 4 x 14
 | SM 1234 analog IN/OUT | AI 4 x 13 bit / AQ 2 x 14 bit
Thermal elements and RTD signal modules | SM 1231 thermal element IN | AI 4 x 16 bit TC, AI 8 x 16 TC
 | SM 1231 RTD | AI 4 x RTD x 16 bit, AI 8 x RTD x 16
Digital signal boards | SB 1221 digital IN | DI 4 x 24 VDC, 200 kHz
 |  | DI 4 x 5 VDC, 200 kHz
 | SB 1222 digital OUT | DQ 4 x 24 VDC, 200 kHz
 |  | DQ 4 x 5 VDC, 200 kHz
 | SB 1223 digital IN/OUT | DI 2 x 24 VDC / DQ 2 x 24 VDC, 200 kHz
 |  | DI 2 x 5 VDC / DQ 2 x 5 VDC, 200 kHz
Analog signal boards | SB 1231 analog IN | AI 1 x 12 bit
 | SB 1231 analog OUT | AQ 1 x 12 bit
Thermal elements and RTD signal boards | SB 1231 thermal element IN | AI 1 x 16 bit TC
 | SB 1231 RTD IN | AI 1 x 16 bit RTD
IO Link Technology | SM 1278 4xIO-Link Master | DI 4x24 VDC or DQ 4x 24 VDC
Weighing technology | SIWAREX | WP231, WP241

## Slide 22: Design and handling S7-1200 load memory
Storing of the tag names and comments in the S7-1200 CPU memory and therefore online, available for project upload, etc.
1, 2 or 4 MB (internal)
Program blocks
Data logs, recipes
Comments
Tag names



## Slide 23: Design and handling Accessories – SIMATIC Memory Card
What can be saved on a S7-1200 memory card?
  Program
  Data
  System data
  Recipes
  Data protocol
  Files
  Projects
  4 MB
  12 MB
  24 MB
  256 MB
  2 GB
  32 GB
  Increased lifespan 500000 write accesses possible
  Project sent as an e-mail with transfer to memory card using standard PC
  No special card reader required (SD card with FAT 32 file system)
  No data lost despite openness with CPU shutdown
  Increased copy protection – Option of linking the programs to the memory card serial numbers
SIMATIC MC optional usable
Capacity
SIMATIC Memory Card

## Slide 24: Design and handling How does the S7-1200 CPU use the SIMATIC memory card?
  For transfer of project and program data into the CPU-internal load memory
  Removal following data transfer  CPU works with the data saved in your load memory.
  For duplication of project and program data in multiple CPUs
  acting as a CPU memory.
  Loss of all project and program data upon removal of a program card from the CPU.
  Replacement and extension of the CPU-internal load memory
Creation of a “transfer card” or “program card” with TIA Portal on a PC with an SD card slot
Program card
Transfer card
Notes: S7-1200 SIMATIC memory card usage
Before programming a memory card the user must ensure that there is a valid network configuration available in your project so that the connection to the AS can be established following installation of the card.
SIMATIC memory cards are preformatted with a SIMATIC memory format which must not be modified. The two concealed files __log__ (system file) and crdinfo.bin (bin file) must not under any circumstances be deleted using a PC. The memory card may not be reformatted on the PC either; it will then be unusable.
The S7-1200 System Manual contains more detailed descriptions on creating and working with a program and transfer card.

## Slide 25: Design and handling SIMATIC S7-1200 accessories
Accessory part | Details
PM1207 Power supply | Inputs: 120/230 V AC 50/60 Hz, 1.2 A / 0.7 A Outputs: 24 V DC / 2.5 A
Battery board | for real-time clock long-term buffering (without CR1025 battery)
CSM 1277 Compact Switch Module | 4 x RJ45 jacks 10/100 MBit/s
Digital SIM 1274 input simulator | 
Analog input simulator | Potentiometer for direct entry of analog value
Extension cable | for 2-row station configuration, 2 m

## Slide 26: Design and handling PM 1207, the power supply for SIMATIC S7-1200
  Optimum integration into the SIMATIC S7-1200 network
    Uniform set-up technology and design
    Universal assembly upon standard profile rail or wall assembly with screws
    Integration in TIA selection tool
  Fixed output voltage of 24VDC  therefore <33V output overvoltage protection. No danger of the user providing “too high voltage” to the CPU.
  2-3 x rated current for 100ms upon startup  for short-term overloads, as the CPU has increased power requirements when switched on
  Thermal design: Can be assembled on the left next to the CPU or communication assemblies with no mandatory clearance, without any negative effect on these (communication/CPU) assemblies through the heat generated through the power supply
  Temperature range up to +60°C WITHOUT derating
  Power failure backup of > 20ms, including with undervoltage at the input (93 / 187 VAC)
  Easy connection to all single-phase networks through automatic range switching - prevents faulty operation
  Slim construction width at 70 mm  saves space in the control cabinet
TECHNICAL DATA:
Input
  Rated voltage AC 120/230 V
    Automatic range switching
    Working range AC 85…132/176…264 V
Output
  Rated voltage 24 V DC +/-3%
    Controlled isolated DC voltage (SELV)
    Ripple/spikes <150/240 mVpp
  Rated voltage 2.5 A
  PowerBoost 2-3 x rated voltage for 100ms upon startup
Additional Information
  Interference emission according to EN 55022 Class B (residential area)
  Ambient temperature 0…+60°C
  Dimensions (W x H x D) in mm: 70 x 100 x 75
  Assembly upon standard profile rail or wall assembly

## Slide 27: SIMATIC S7-1200 configured in the TIA Portal Modular and powerful.
  STEP 7 Basic is integrated software for logic, HMI and networking with a common editor – Overall navigation and all icons and menus are uniform in all views. Easy to learn and therefore saves time
  Automatic detection and load concept – Extremely fast hardware configuration in the development stage, all documentation is saved in the CPU (icons, comments, descriptions), far easier and more rapid maintenance
  No separate standalone software programs - (And no separate configuration maintenance) for PID controller or motion control with PLC open instructions. Everything is integrated into the engineering software and is part of the user program
  Engineering software innovations for the SIMATIC S7-1200 …
Integrated automation software for all your automation tasks
Notes: 3. Software Innovation
The most significant breakthrough for this product line is the Step 7 Basic programming software
The industry first One Software – One User Program for Controller, HMI, and Networking This type of integrated functionality has never been available in traditional Micro or Nano PLCs. Only commonly found in much larger controller classes, Specialized or PC-Based Control packages.
All configuration begins from the Central Navigation Portal. Easy to start and efficiently manage projects, no separate icons for each Add-On
Common navigation layout for each editor, I/O Config, Logic, HMI Config, Motion, Networking, PID Tuning. Consistent navigation, easy to learn and remember
All editors are drag-drop interactive, all in the same instance. No need to save/close or import/export between them.
The New Step 7 Basic provides Integrated Automation development software specifically for the Compact Controller class

## Slide 28: Efficient engineering S7-1200 interrupt structure
OS
Interrupt - processing
Hardware
Cyclical
Startup
Process
Diagnostics
Time
OB1
OB 100
OB 20x
OB 20x
OB 82
FC
FC
FC
FC
Global
Global
FB
Instance
FB
Instance
FC
FC
The assignment of events to OBs can occur during configuration or at runtime
As with S7-1500 all OBs are interrupt-capable as standard, but all OBs (expect for OB1) can be configured as not interrupt-capable.

## Slide 29: Efficient engineering Recipes and data logging
  Input recipes via *.csv file and save on card
  e.g. Machine configuration, initial values, tool-dependent configuration data
  Storing of the data in the *.csv file on a memory card or internal memory
  Upload & download of the recipes via Webserver
  Recipes
  Cyclical & event-triggered storage of tags, incl. string tags
  e.g. Saving of operating data, error information, ....
  Storing of the data in the *.csv file on a memory card or internal memory
  Archive downloads via Webserver
  DataLog (archive)

## Slide 30: Efficient engineering Configuration control (option handling) in the central setup
  Different hardware configurations provided in the controller:
    Configuration modified in the user program (OB100 startup)
    Options added on at the end of the configuration
  Support for CM/CP/SB/CB/SM with S7-1200
  Configuration control in the central setup
Maximum configuration:
Options:
A, B, C, D
A
B
C
D
Configuration upon delivery:
Options:
A, D
Machine update:
Options: A, D, C
A
D
A
C
D

## Slide 31: SIMATIC S7-1200 configured in TIA Portal Highlight performance
Comprehensive network options to meet your requirements!
  PROFINET Master – decentralized Profinet architectures possible for I/O, HMI, drives, and other Profinet field devices. NO communication module required!
  PROFIBUS Master & Slave – decentralized Profinet architectures possible for I/O, drives, and other Profinet devices, including integration into existing system networks.
  AS-i Master – The new AS-i-Master is configured in full in the TIA Portal and a new AS-i network can be created very easily with just a few clicks. AS-i networks do not therefore require separate software!
  CANopen Master – Enables connection with CANopen devices, as well as with devices running Transparent CAN 2.0A.
  Comprehensive network options for SIMATIC S7-1200

## Slide 32: SIMATIC S7-1200 configured in TIA Portal Highlight performance
Comprehensive network options to meet your requirements!
  Modbus TCP – Enables communication with devices as Modbus master or slave. Only one TCP function block is required for this.
  IO-Link Master – Fast and easy integration of the SIRIUS compact starter, M200D starter and SIRIUS soft starter for simple starter control.
  GPRS/LTE module – Easy implementation for data recording and control of decentralized computer.
  TCP/IP – Via the instructions for open communication you can communicate with other CPUs, other PCs and with devices that use TCP/IP communication protocols as standard. NO communication module required!
  Comprehensive network options for SIMATIC S7-1200

## Slide 33: SIMATIC S7-1200 in the TIA Portal Highlight performance
Comprehensive network options to meet your requirements!
  RS-485, RS-422 & RS-232 – The S7-1200 CPU supports point-to-point (PtP) communication for character-based serial protocols, and this provides maximum freedom and flexibility for the use of PtP communication instructions in the user program.
  Modbus RTU – Using the Modbus instructions the Modbus master or slave is able to communicate with devices that use the Modbus RTU protocol.
  USS – Using simple USS instructions you can control the operation of drives that support the USS (Universal Serial Interface) protocol
  Comprehensive network options for SIMATIC S7-1200

## Slide 34: Communication S7-1200
CPU
SM
CM CP
SM 1278
CB 1241 RS485
SINAMICS V20
USS MODBUS RTU
Module | Communication | 
CM 1241 | RS232 | serial
CM 1241 | RS422/485 | serial
CM 1243-2 | AS-i master | 
CM 1242-5 | PROFIBUS | DP slave
CM 1243-5 | PROFIBUS | DP master
CP 1242-7 | GPRS | Mobile communications telecontrol
CP 1243-7 | LTE | Mobile communications telecontrol
CP1243-1 | Ethernet | VPN/Firewall, Telecontrol Ethernet (DNP3, IEC 60870)
RF120C | RFID | 1 Reader port; RS422
CM CANopen | CANopen | 3rd party: HMS
Notes: S7-1200 | CPU Digital I/O | CPU Analog I/O | CPU Power supply and I/O type
CPU 1211C | 6 IN - 4 OUT | 2 IN | Available in three designs for CPU power supply / input / output type DC / DC / DC AC / DC / relay DC / DC / relay
CPU 1212C | 8 IN – 6 OUT | 2 IN | 
CPU 1214C | 14 IN -10 OUT | 2 IN | 
CPU 1215C | 14 IN -10 OUT | 2 IN - 2 OUT | 
CPU 1217C | 10 IN sink/source 4 IN 1.5V differential 6 OUT MOSFET Sourcing 4 OUT 1.5V differential | 2 IN - 2 OUT | Only available as DC / DC / DC
S7-1200 communication options
Integrated PROFINET network connection
CB 1241 RS485
CM 1241 RS232
CM 1241 RS485
CM 1241 RS422/485
CP 1242-7 GPRS
CM 1242-5 PROFIBUS slave
CM 1243-5 PROFIBUS master
CM 1243-1 DNP3 Ethernet WAN
CM 1243-1 IEC Ethernet WAN
CP 1243-1 Ethernet WAN (Firewall and VPN)
CM 1243-2 AS-I Master
RF120C RFID
TS Adapter and modular TS Adapter for SIMATIC Teleservice

## Slide 35: Communication S7-1200 integrated PROFINET (Ethernet) interface
S7-1200 CPUs use PROFINET connections to STEP 7, S7-1200 CPUs and HMI panels
… with the STEP 7 software
  CPU hardware configuration
  Loading a project
  Monitoring/amending runtime tags
  Set runtime I/O statuses
  Diagnostics information
... with HMI panels
  Data from or to the CPU
  System diagnostics
... from CPU to CPU
  Open communication with T-block instructions
  Supported protocols: TCP/IP, ISO on TCP, UDP, S7 Com. (PUT/GET)
  Communication ...
Notes: S7-1200 Ethernet communication
The PROFINET port for the CPU supports simultaneous communication connections:
OPC Server (Object Linking and Embedding – OLE) for Process Control Server. OPC functionality is possible with the SIMATIC NET OPC server.
PROFINET functionality including controller and device
The S7-1200 Ethernet interfaces are designed as PROFINET and support PROFINET IO and iDevices.
Communication with third-party devices via Ethernet is supported. The S7-1200 provides a “native” Ethernet-TCP/IP protocol (“FreePort” for Ethernet) for user-specific development of this functionality. Communication is possible with third-party PLCs if these support the same Ethernet connectivity as S7-1200.
 | Programming device (PD) | Human Machine Interface (HMI) | GET/PUT Client/Server | Open user communication | Web browser
Maximum number of connection resources | 3 guaranteed to support 1 PD | 12 guaranteed to support 4 HMI devices | 8 | 8 | 30 guaranteed to support 3 web browsers

## Slide 36: Communication MRP - Media redundancy protocol
Based on ring topology (IEC 61158-5-10)
Max. 50 nodes in the ring
  PROFINET IO-Controller
  PROFINET IO-Devices
  Components of the network infrastructure (IE switches)
200 ms reconfiguration time
CPU 1215/17 as MRP Client at least FW V4.1
Configuration and diagnostics in STEP7
Industrial Ethernet
PROFINET
    Improved plant availability
    More flexibility
    Lower costs since less equipment required
S7-1500
> V4.1
< V4.2
S7-1200

## Slide 37: Communication S7 routing
Enables a connection between different subnets
A SIMATIC S7-1200 station acts as an S7 router
Based on PROFINET
Actually only with CP 1243-1 at least V2.0 (6GK7243-1BX30-0XE0) and CPU FW V4.2
192.168.0.1
192.168.0.3
177.168.0.1
192.168.0.2
S7 routed
Connection
Subnet 1
Subnet 2
Routing between the CPU and a CP, e.g. for transfer an HMI project from ES to panel
S7-1500
S7-1200

## Slide 38: Communication Webserver
Simple location-independent information recording for process variables and system status
Integrated Web server
  Access to system and process reports as well as identification data
  System diagnostics for all configured assemblies centrally and decentralized
  Communication diagnostics on parameters, statistics, connection status
  Access to process data via tag tables and freely definable tag lists
  Pages to be defined by the user
  Firmware update
Archive
  Access via Webserver using Filebrowser for reciprocal exchanges of data in .csv format
  Logging of user-defined tags
  Communication ...

## Slide 39: Communication Station webserver
Various types of communication access: CPU PN interface, CP 1243-7 LTE, CP1242-7 V2
Central access via CPU page independently of the interface
User is then able to browse to the CP-specific webpages from there
uniform, consistent webserver for entire S7-1200 station
Remote access via Internet/mobile communications
PN access

## Slide 40: Communication SIMATIC apps
Description:
Secure access via app to the webserver for your SIMATIC S7-1200/1500 and ET200SP
Supported firmware:
SIMATIC S7-1200: V3.0 or higher
SIMATIC S7-1500/ET200SP: V1.8 or higher
Functions:
Detect up to 50 networked CPUs via HTTPS and established a connection
Change CPU operating mode (RUN/STOP)
Read out CPU diagnostics information and send via e-mail
Change tags
Monitor up to 8 tags in the curve display
High security: 1. Encrypted communication (AES256) 2. Encrypted profile data
3. Password required when starting the app
4. Password required to establish the connection
SIMATIC S7 App (Q2/2015)

## Slide 41: Communication PROFINET i-Device
  Simple configuration of S7-1200 CPUs in a master/slave architecture through reading and writing the reciprocal I/O images
  Connection of CPUs in different projects
  NO PN-PN coupler required (transparent network)
IO controller
CPU1
IE / PROFINET
IO device
Operational system
Application / user program
IO process image
Input addr.
Output addr.
Operational system
Application / user program
IO process image
Input addr.
Output addr.
PROFINET IO
IO controller 1
IO device 2
IE / PROFINET
IO device 1
IO device 3
i-device
Savings with costs / installation / wiring of additional hardware
CPU2

## Slide 42: Communication Shared I-Device
  Access for up to 2 controllers on S7-1200 as i-device
  Rapid exchange of data in real time between S7-1x00 CPUs
  Incorporation of 3rd party controllers under PROFINET
As of V4.1
Controller 1
Controller 2
  Shared I-device

## Slide 43: Communication Serial communication
RS485/422
RS232
  ASCII protocol (character-based serial communication) uses STEP 7 PtP instructions
  USS Drive protocol is programmed with STEP 7 USS library instructions
  MODBUS protocol is programmed with STEP 7 MODBUS library instructions
  3964R Protokoll
  S7-1200 CPU communication via RS232 and RS485 connections
Use of RS232 and RS485/422 modules CM1241 or RS485 Signalboard CB1241 for PtP communication
Notes: Serial communication with the S7-1200
MODBUS RTU is possible for both RS485/422 and RS232 signal modules.
The USS library is supported on the RS485 port and is included in STEP 7 Basic.
The CM 1241 RS232 module supports handshaking.
The S7-1200 RS232 and RS485/422 modules feature galvanically isolated connections.

## Slide 44: Communication USS drives
Update rate
  Fixed update rate (as fast as possible)
  Enable instructions in an interrupt alarm OB in order to set a user-defined update rate.
Support for drives
  Maximum 15 drives per CM (communication module) supported
  Non support:
    MM3 drives
    Deregistration of missing drives
  PZD parameters – Up to eight user-defined PZD parameters for control and speed

## Slide 45: Communication IO-Link support
  S7-1200 CPU up to 8 IO-Link master modules - centralized
  Data rate COM1 (4.8 kbaud), COM2 (38.4 kbaud), COM3 (230.4 kbaud)
  Standard IO Mode (SIO Mode)
  up to 4 IO‑Link devices (3 wire) or 4 standard actuators
  Diagnostics configurable for each port
  I&M identification
  IO‑Link parameter allocation with S7‑PCT (Port Configuration Tool) V3.2
  IO link master specification V1.1

## Slide 46: Communication SM 1278 4xIO-Link master (6ES7 274-1XK30-0XA0)
  Point-to-point connection, no bus system
    Existing wiring topologies are retained
  Standard sensor/actuator cable (three wires with one signal wire), unshielded, 20 m in length, no special-purpose cable / connector
  Manufacturer-independent communication standard for the PNO
  Non-stop consistent communication
    Cyclical, bidirectional process data communication (typ. 2 ms cycle)
    Non-cyclical service data transmission between sensors/actuators and the controller as required
  Integrated differentiated diagnostics alarms
   Link
Switching devices
<20 m
Control cabinet
<20 m
3RA6 compact starters
3RA27 function modules for feeders
3UG4 monitoring relays
3RW40 soft starters

## Slide 47: Communication IO-Link Support  Engineering

## Slide 48: Communication SIMATIC RF120C – Fast communication module
Integration in TIA Portal (from V12 SP1)
  Full integration into the device configuration for the TIA Portal
  Simple function blocks for fast programming
One reader per RF120C
  So that the data is available to the application immediately
  Up to three RF120C can be operated in parallel to the left of the CPU
Reader cable
  Submin-D connector on RF120C;
  Ready-made cables are available
Firmware update via SIMATIC Manager
  Rapid bug fixes via ONLINE update (up to the reader)
Order number: 6GT2002-0LA00
S7-1200 and RF120C: cost-effective and powerful identification solution

## Slide 49: Communication SIMATIC RF120C – Fast communication module for S7-1200
RF120C | 
Interface to the application | Internal S7 bus
Connection technology | S7-1200 setup technology; screw terminals for 24 V supply
Interface to the reader | RS422 incl. 24 Volt; up to 115.2 KBaud
Connection technology | Submin-D connector
RFID system | RF200, RF300, RF600, MOBY D/U, MV400
FB, driver | Instructions: Read, Write, Read_EPC-Mem, Write_EPC-Mem, Set_Ant_RF300, Set_Ant_RF600, Reset_Reader; based on FB101
Number of readers | 1 per RF120C; 3 per S7-1200
Degree of protection | IP 20
Dimensions (W x H x D) | 30 x 100 x 75

## Slide 50: SIMATIC S7-1200 SIWAREX WP231 – Basic applications
  Level measurement in silos and bunkers
  Plattform scales
  Force and tension measurements
  Typical industries: Food & Beverage, Chemicals, Cement, Aggregate
  Legal for trade certificate according OIML-R76
  Applications:
  CPU 1212C  up to two SIWAREX modules
  CPU 1214C or higher  up to eight SIWAREX modules
  Full parameter access from the CPU via free downloadable function block  Complete commissioning and calibration via CPU/HMI
  Supported S7-1200 CPU:
  Up to eight parallel connected analog 350 Ohm load cells per SIWAREX (1mV/V, 2mV/V, 3mV/V or 4mV/V)
  1 SIWAREX = 1 scale
  4 digital inputs / 4 digital outputs
  1 analog output
  Ethernet (Modbus TCP & SIWATOOL)
  RS485 (Modbus RTU)
  Connection options:

## Slide 51: SIMATIC S7-1200 SIWAREX WP241 – Belt weigher applications
  Belt scales (Cement-, Aggragate plants, Mines, Food & Beverage plants)
  Weigh feeder applications (Food & Beverage, Chemical, Steel)
  Applications:
  CPU 1212C  up to two SIWAREX modules
  CPU 1214C or higher  up to eight SIWAREX modules
  Full parameter access from the CPU via free downloadable function block  Complete commissioning and calibration via CPU/HMI
  Supported S7-1200 CPU:
  Connection options:
  Up to eight parallel connected analog 350 Ohm load cells per SIWAREX (1mV/V, 2mV/V, 3mV/V or 4mV/V)
  1 SIWAREX = 1 scale
  3 digital inputs / 4 digital outputs / 1 speed sensor input
  1 analog output
  Ethernet (Modbus TCP & SIWATOOL)
  RS485 (Modbus RTU)

## Slide 52: SIMATIC S7-1200 SIWAREX WP251 – Dosing , Batching and Bagging applications
  Dosing and batching scales (Chemical-, Food-, Pharma, Packaging industries)
  Bagging machines (Bulk solids industries)
  Eichfähig gemäß OIML-R51, R61 und R76
  Applications:
  CPU 1212C  up to two SIWAREX modules
  CPU 1214C or higher  up to eight SIWAREX modules
  Full parameter access from the CPU via free downloadable function block  Complete commissioning and calibration via CPU/HMI
  Supported S7-1200 CPU:
  Connection options:
  Up to eight parallel connected analog 350 Ohm load cells per SIWAREX (1mV/V, 2mV/V, 3mV/V or 4mV/V)
  1 SIWAREX = 1 scale
  4 digital inputs / 4 digital outputs
  1 analog output
  Ethernet (Modbus TCP & SIWATOOL)
  RS485 (Modbus RTU)
  RS485 (Modbus RTU)

## Slide 53: Communication Controller Area Network CANopen 021620-B
  A CANopen connection to a S7-1200 system enables integration between devices and the S7-1200 system
  Up to 3 CANopen modules per S7-1200 CPU
    Connection type to the CAN: 9-pin DSUB (male)
  Up to 16 CANopen nodes per module
  256 bytes each for inputs and outputs with the CANopen module
  Can be integrated in the hardware catalog of the TIA Portal configuration suite
  Ready-made function blocks for simple PLC programming available in the TIA Portal
   Link
  SIMATIC S7-1200C CANopen master/slave
Easy integration in CANopen applications

## Slide 54: Communication MODBUS communication
  Use of a CM or CB 1241 module for serial communication
  MODBUS instructions of the communication module for simplified MODBUS RTU operation.
    MB_COMM_LOAD for basic initialization of the master and slave operation
    MB_MASTER and MB_SLAVE for controlling the report and connection allocations
  Modbus addressing supports a maximum of 247 slaves (slave numbers 1 to 247).
  Maximum of 32 devices per segment in the Modbus network depending on the loading and drive functions of the RS485 interface
  Repeater required if using more than 32 devices to extend to the next segment
  MODBUS RTU protocol
  Open User Communication MODBUS TCP instructions use the PROFINET port integrated in the CPU
  MODBUS TCP protocol

## Slide 55: Communication Overview of CP 1243-1 product features
  Communication Processor for connecting S7-1200 to Ethernet network with additional Interface and security features firewall and VPN. Integration to Scada Systems via Telecontrol Protokolls (DNP3, IEC 60870, Telecontrol Basic).
  Single-width S7-1200 enclosure (30 x 110 x 75)
  Temperature range in operation: -20°C to +70°C
  Standard rail mounting
  Diagnostic LEDs (overall status and detail)
  Power supply using backplane bus
  1 x Ethernet Port RJ45 (10/100 Mbit/s) for connecting a modem/router such as SCALANCE M
  Integrated security functions (VPN and Firewall)
  Integration to Scada Systems via Telecontrol Protokolls (DNP3, IEC 60870)
  CP1243-1 (6GK7243-1BX30-0XE0)

## Slide 56: Communication Overview of CP 1243-7 product features
  1 connection to LTE (4G) mobile network (different versions for EU and North America)
  Single-width S7-1200 enclosure (30 x 110 x 75)
  Temperature range in operation from -20ºC to +70ºC
  Standard rail mounting
  Diagnostic LEDs (overall status and detail)
  Integrated security functions (VPN and Firewall)
  Access to the CPU Webserver
  Email and SMS Alarms
  Process Monitoring and Control via Cellular network
  CP1243-7 (6GK7243-7KX30-0XE0 – EU version 6GK7243-7SX30-0XE0 – US version)
Communication processor to connect SIMATIC S7-1200 via LTE (4G) mobile network to control point system with TeleControl Server Basic

## Slide 57: SIMATIC S7-1200 PROFIBUS communication DP master CM 1243-5 and DP slave CM 1242-5
PROFIBUS DP-Master CM 1243-5
  Connection for up to 16 DP slaves
  PG/OP communication: up to 4 connection for HMI and 1 connection for PG
  S7 communication: 4 S7 connections to other S7 stations with PUT/GET
PROFIBUS DP-Slave CM 1242-5
  as an intelligent DP slave for communication for the S7-1200 with any other DP master
  Communication for S7-1200 CPUs according to PROFIBUS standard IEC61158/61784

## Slide 58: SIMATIC Integrated Technology S7-1200 / S7-1500 – integrated compact controllers
  Continuous PID controller for proportional-acting actuators
  Analog or pulse-width modulated (PWM) output
  PID Compact
  PID controller for integrating actuators (e.g. valves) with digital signals for opening and closing
  Output for analog and binary valve control
  Position feedback/ stop signal
  Integrated motor regulating time measurement
  PID 3-Step
  Closed-loop control structures: PI, PID
  Inversion of control direction, anti-windup and weighting of P and D portion
  Actual value scaling, alarms for actual and target values
  Manipulated variable limitation
  Parameter setting for conduct in the event of fault
  Two-stage optimization procedure with optimization in the operating point
  Technical features

## Slide 59: SIMATIC Integrated Technology S7-1200 / S7-1500 – integrated compact controllers
Cost savings through integrated PID controllers with premium auto-tuning
  For versatile control tasks
  Continuous controllers and step controllers
  Automatic determination of the controller parameters
  Manageable configuration screens
  Commissioning screens with integrated trace
  Available in S7-1200 and S7-1500 (integrated in FW)
  Integrated PID controllers

## Slide 60: SIMATIC Integrated Technology S7-1200 / S7-1500 – integrated compact controllers
  Two controller parameter sets for heating and cooling – alternatively: cooling factor
  Analog or pulse-width modulated control signals for heating and cooling
  Integrated two-stage self-optimization – specifically for temperature processes
  Heating and cooling optimization available separately (multi-zone applications)
  Deadband and control zone can be set
  Cascade control with anti-windup
  PID Temp – Temperature controller for actively heating and cooling a process
Notes: Active heating and active cooling elements are frequently used to control the temperature.
The temperature controller provides two separate outputs for connecting the actuators. The temperature controller used two separate PID parameter sets in order to account for the response times of the heating and cooling elements which are generally very different. These allow more rapid and precise controls.
Extrusion systems in the plastics industry:
plastic granules are fused via different temperatures zones. The first zones can normally be heated as well as cooled.
The temperature controller also provides synchronization mechanisms for control optimization for such applications.
Cascade control: multiple control loops are ‘nestled’ in each other (in the image: chocolate melting)
Advantages: improved fault response, subordinate control loops have a linearizing effect

## Slide 61: SIMATIC Integrated Technology - PID Control S7-1200 / S7-1500 – integrated compact controllers
 | Memory requirements for the instance DB |  | CPU processing time (typical) | 
PID Compact | Load memory approx. | 12000 bytes | CPU 121xC (FW>=4.1) | 300 µs
 | Work memory | 788 bytes |  | 
 | Residual work memory | 44 bytes | CPU 1511/16/18 (FW>=1.7) | 85/50/4 μs
PID 3-Step | Load memory approx. | 15000 bytes | CPU 121xC (FW>=4.1) | 410 µs
 | Work memory | 1040 bytes |  | 
 | Residual work memory | 60 bytes | CPU 1511/16/18 (FW>=1.7) | 120/65/5 μs
PID Temp | Load memory approx. | 17000 bytes | CPU 121xC (FW>=4.1) | 580 μs
 | Work memory | 1280 bytes |  | 
 | Residual work memory | 100 bytes | CPU 1511/16/18 (FW>=1.7 | 130/75/6 μs

## Slide 62: SIMATIC S7-1200 Technology integrated
  Flexible drive connection via PROFINET, PROFIBUS or analog interfaces
  CPU 1217C with 1.5 V differential outputs for speed and position control up to 1 MHz
  Easy programming of the motion processes with PLCopen Motion Control blocks
  Uniform configuration for controller/HMI/drives
  Convenient diagnostics and commissioning tools (control panel, trace)
  Easy troubleshooting using automated alarm messages to the engineering system
  Wizard for motion control technology with PTO/PWM
  Control functionality
Easy scalability through integration of the same Motion Control functions in all controllers

## Slide 63: SIMATIC S7-1200 Technology integrated - Possible drive versions
Step-motor drive
or servo drive
Servo inverter
Controlled operation via Pulse-Train Interface (PTO)
  Simple onboard interface without position feedback
  Number of drives dependent on the CPU type
  For step-motor drives or servo drives with pulse interface
Position-controlled operation
  Can be used on all CPU types
  HSC possible as encoder connection
  Up to 8 drives
  Absolute value encoders supported (no overflows permitted)
PROFIdrive drives
  For all Sinamics PROFINET/PROFIBUS drives
  Servo or frequency inverter
Analog drives
  Plenty of analog Siemens and third-party drives available
PTO signal
Enable
Ready
Motor
Power
Drive
PLC
PTO signal
Enable
Ready
Motor
Power
Drive
PLC
Encoder
Encoder data
Data exchange
Notes: Background:
There are only a few Siemens drives that can be connected via PTO
This is also not possible with all 1200 CPUs, and only with the DC/DC/DC version or via special signal boards
Position-controlled axes is therefore the real method for connecting all 1200s with drives as openly as possible
Difference with 1500:
Never isochronous
Incremental encoders can be connected cost-effectively to the CPU (HSC)

## Slide 64: SIMATIC Technology integrated Counting and measuring with high-speed counters (HSC)
Incremental encoder
. . .
 | 1214C | 1217C
Max. number of HSCs permitted | 6 | 6
1 MHz max. single-phase | 0 | 4
1 MHz max. A/B counter | 0 | 2
100 kHz max. single-phase | 6 | 6
80 kHz max. A/B counter | 3 | 3
30 kHz max. single-phase | 4 | 4
20 kHz max. A/B counter | 2 | 2
The two-phase or A/B rotary encoder is the incremental encoder most often used as a result of its improved accuracy.

## Slide 65: SIMATIC Technology integrated High speed counter HSC - Gate input
Use case: Measurement of components on a conveyer.
Advantage: Measurements can be realized easily. Since FW 4.2 are no additional OBs necessary (OBs = interrupts).
After the probe was passing the light barrier the length is measured. Independent of incoming pulses the last value is fix on the input double word.
Gate
Count
Notes: Z.B. zur Messung von Rundhölzern oder Kanthölzern mit einer Lichtschranke (Gate Eingang) und einem Drehgeber am Förderband. In FW >V4.2 mussten für Steigende und Fallende Flanke der Lichtschranke ein OB zum auslesen des Zählwertes „:P“ Projektiert werden. Durch Wegfall der OB Laufzeit ist die Genauigkeit deutlich verbessert

## Slide 66: SIMATIC Technology integrated High speed counter HSC - HSC Output
Use case: exact marking of components
Advantage: A output can activated easily. There is no additional OB necessary since FW 4.2 (OBs = interrupt) .
After pulse time was running the output is reasserted without user program action
Output
Gate
Count

## Slide 67: SIMATIC Technology integrated High speed counter HSC - Capture input
Use case: capture input
Advantage: This feature copy the current counter value to the capture register with change on an digital input. The Register investigation can be done later on without using any additional interrupt OBs
Gate
Count
Capture
Notes: Z.B. zur Messung von Rundhölzern oder Kanthölzern mit einer Lichtschranke (Gate Eingang) und einem Drehgeber am Förderband. In FW >V4.2 mussten für Steigende und Fallende Flanke der Lichtschranke ein OB zum auslesen des Zählwertes „:P“ Projektiert werden. Durch Wegfall der OB Laufzeit ist die Genauigkeit deutlich verbessert

## Slide 68: SIMATIC Technology integrated PWM Pulse-width modulation - Flexible frequency output
Function: Flexible frequency output
Use case:
Simulation of single phase encoders
Output of an analogue value as frequency
Generating of sound
Stroboscope for rotary speed check or product detection
Laser cutting, frequency (for die wave length) and also pulse with (for power) can adjusted.
Cluing, numbers and size of clue dots can be changed
variable frequency
30
20
10
50 50
50 50
50 50
fix pulse/pause relation
since FW4.2
30
20
10
50 50
60 40
80 20
Fix pulse/pause relation
variable frequency
since FW4.2

## Slide 69: SIMATIC Technology integrated High speed counter HSC plus PWM - Test setup
Use Case: the length and the speed of an component should be measured
Solution: Pulse output create 100kHz which are connected to the HSC count input. The inputs Gate, Capture, Sync are connected to light brakes. The calculation of speed and length can be done in a slow main cycle. No additional hardware OB is necessary
Gate
Count
Capture
Sync bei steigenderFlanke
PWM out 100KHz
50,8mm

## Slide 70: SIMATIC Technology integrated Period measurements with high-speed counters (HSC)
Multiple counter events in one measurement interval
Zero and one counter event in multiple measurement intervals

## Slide 71: Integrated system diagnostics
Efficient fault analysis through a uniform display concept
  Integrated system diagnostics for the centralized setup are active by default. You only configure the following as required: checkbox for high/low analog range, wire breakage, power failure, etc.
  Automated updated of the diagnostics information with new HW components, no additional effort required
  System diagnostics information possible in the CPU-STOP
  Configuring instead of programming
  Uniform clear text information in the TIA Portal, Webserver, HMI & SIMATIC app
  Uniform display concept

## Slide 72: SIMATIC S7-1200 Diagnostics in real time - Trace for the S7-1200
  Recording of up to 16 different tags in separate CPU memory
  Up to 2 independent trace jobs supported simultaneously
  Cycle-granular recording (real time) so that no value is lost
  Versatile trigger conditions for filtering out the event
  Recording takes place independently of the engineering system on the CPU for simple searches of sporadic faults
  Exportable measurements for documentation and user-specific processing (csv and ttrec file)
Program and application diagnostics in real time for detection of sporadic faults

## Slide 73: SIMATIC S7-1200 Trace - Repeated measurements stored on memory card
Repeated measurement
Record N measurements according trigger conditions
Activate the trace after completing a measurement
Option: overwrite the oldest measurement
Up to 1000 measurements on card
Measurements stored on SMC
Persistent storage of measurements
Significantly more Trace Data for established Analysis
Customer benefit
S7-1500
S7-1200
TIA Portal
Webserver
RAM*
CPU
onlyS7-1500
*excl. f. Traces

## Slide 74: Security Integrated Increased know-how protection in STEP 7
  Password protection from unauthorized opening of the program blocks with STEP 7 and therefore protection from unauthorized copying or e.g. developed algorithms
  Password protection from unauthorized evaluation of the program blocks with external programs
    from the STEP 7 project
    from memory card data
    from program libraries
Protection of intellectual property and investments made

## Slide 75: Security Integrated Increased copy protection
  Linkage of individual blocks to the serial number for the memory card or CPU
  Protection from unauthorized copying of program blocks with STEP 7
  Protection from unauthorized duplication of the configuration on the memory card
Protection from unauthorized reproduction of executable programs

## Slide 76: Security Integrated Dynamic copy protection with mandatory password
  Static linkage: direct configuration of a target serial number (from memory card or CPU) for program blocks
  Dynamic linkage: automatic detection of a target serial number with linkage to this target serial number during the download on the CPU or memory card
  Copy protection with different methods for providing a target serial number:
  Both cases involve linkage of the block to a special HW serial number for the CPU or the memory card
  A block with dynamic linkage in the TIA Portal project is not tied to a certain serial number but is protected via an additional password for copy protection (from STEP 7 V13 SP1)
    Automatic serial number configuration and simple linkage for machine manufacturers
    Simple mass download with copy protection for authorized person only
  Advantages:
As of V4.1
Program block with static linkage
Program blocks with dynamic linkage
12345678
Target serial number:
and
Automatic detection
TIA Portal Project
Download with check of the serial number by the controller
Download with auto- matic integration of the serial number by the TIA Portal
S7 Controller
Program blocks with active copy protection
12345678

## Slide 77: Security Integrated Increased manipulation protection
  Improved protection from manipulation of the communication with access to the controller by digital checksums
  Protection from network attacks such as infiltration of fake / recorded network communication (replay attacks)
  Protected transfer for passwords upon authentication
  Detection of manipulated firmware updates through digital signatures
Protection of communication from unauthorized manipulations for maximum system availability

## Slide 78: SIMATIC Technology integrated Extended Know How protect - Copy prevention external load memory
  Optional – protection against copy the project by using a transfer card
Prevention unauthorized project copy
Use a transfer SD card to recover the use of the CPU for a customer that has forgotten his password.
Notes: an empty SD card (no Job file) causes no CPU action. ILM is not copied to ELM and ILM is not erased.
a blank PROGRAM SD card causes no CPU action. ILM is not copied to ELM and ILM is not erased.
a transfer SD card (TO_ILM) causes the CPU to replace ILM with the contents of ELM.
No change in the evaluation of any other SD card types.

## Slide 79: Security Integrated Access protection
Comprehensive protection against unauthorized configuration changes.
  via Security CP 1243-1 through integrated Firewall and VPN
  Extended access protection

## Slide 80: Safety integrated S7-1200 Failsafe …a unique, innovative and efficient safety solution
  Type and part reduction
  Standard and fail-safe automation with just one controller
  PROFINET integrated
+
  investment protection
  Extend existing system simply with Safety
  Simple porting of existing user programs between S7-1200 <> S7-1500
+
  Certified in accordance with EN 61508 2nd Edition up to SIL 3 and EN ISO 13849-1 up to Pl e
  Established coded processing instead of multi-processor system
+
  Maximum manipulation protection
  Additional password protection for access to F configuration and F program
+
  Integrated diagnostics
  Rapid fault finding via granular reporting in clear text …including globally via WEBserver
+
Notes: 80

## Slide 81: Safety integrated SIMATIC S7-1200 Failsafe portfolio
  CPU 1212FC DC/DC/DC
  CPU 1212FC DC/DC/Rly
  CPU 1214FC DC/DC/DC
  CPU 1214FC DC/DC/Rly
  CPU 1215FC DC/DC/DC
  CPU 1215FC DC/DC/Rly
  Failsafe S7-1200 CPUs
  SM 1226 F-DI 16 x 24VDC
  SM 1226 F-DQ 4 x 24VDC
  SM 1226 F-DQ 2 x Relay
  Failsafe S7-1200 IO modules
  Fail-safe S7-1200 and S7-1500 supported
  Graphical user interface (GUI), online help:
  Documentation:
  STEP 7 Safety Advanced V14 SP1
  Functional such as Safety Advanced for fail-safe S7-1200
  Graphical user interface (GUI), online help:
  Documentation:
  STEP 7 Safety Basic V14 SP1

## Slide 82
siemens.com
Subject to changes and errors. The information given in this document only contains general descriptions and/or performance features which may not always specifically reflect those described, or which may undergo modification in the course of further development of the products. The requested performance features are binding only when they are expressly agreed upon in the concluded contract.
All product designations, product names, etc. may contain trademarks or other rights of Siemens AG, its affiliated companies or third parties. Their unauthorized use may infringe the rights of the respective owner.